## Par_AvailableExcessHeat
Info: kilde: https://www.energy.gov/eere/amo/articles/waste-heat-recovery-publications-and-resources - :
Benevning: andel av total load av heat
AvailableExcessHeat
0.2

## Par_CarbonIntensity
Info: For CH4 og biogass: https://www.miljodirektoratet.no/ansvarsomrader/klima/for-myndigheter/kutte-utslipp-av-klimagasser/klima-og-energiplanlegging/tabeller-for-omregning-fra-energivarer-til-kwh/, For Strøm: https://www.nve.no/nytt-fra-nve/nyheter-energi/lavt-klimagassutslipp-knyttet-til-norsk-stroemforbruk-i-2022/
Benevning: | [kgCO2e/MWh]
Technology | OperationalMode | CarbonIntensity
Power_Grid | 1 | 19
Power_Grid | 2 | 0
ElectricBoiler | 1 | 0
ElectricBoiler | 2 | 0
HP_LT | 1 | 0
HP_MT | 1 | 0
HP_MT | 2 | 0
PV | 1 | 1
P2G | 1 | 0
G2P | 1 | 0
GasBoiler | 1 | 160
GasBoiler | 2 | 160
GasBoiler | 3 | 200
GasBoiler | 4 | 200
GasBoiler | 5 | 1
GasBoiler | 6 | 1
GasBoiler_CCS | 1 | 0
GasBoiler_CCS | 2 | 0
GasBoiler_CCS | 3 | 0
GasBoiler_CCS | 4 | 0
GasBoiler_CCS | 5 | 0
GasBoiler_CCS | 6 | 0
CHP | 1 | 160
CHP | 2 | 160
CHP | 3 | 200
CHP | 4 | 200
CHP | 5 | 1
CHP | 6 | 1
CHP_CCS | 1 | 0
CHP_CCS | 2 | 0
CHP_CCS | 3 | 0
CHP_CCS | 4 | 0
CHP_CCS | 5 | 0
CHP_CCS | 6 | 0
Biogas_Grid | 1 | 0
Biogas_Grid | 2 | 0
CH4_Grid | 1 | 0
CH4_Grid | 2 | 0
CH4_H2_Mixer | 1 | 0
DieselReserveGenerator | 1 | 265
H2_Grid | 1 | 0
H2_Grid | 2 | 0

## Par_CostEmission_1_2025
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.069402

## Par_CostEmission_1_2050
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.18974

## Par_CostEmission_2_2025
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.18333

## Par_CostEmission_2_2050
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.77684

## Par_CostEmission_3_2025
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.052051

## Par_CostEmission_3_2050
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.12479

## Par_CostEmission_4_2025
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.18333

## Par_CostEmission_4_2050
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.77684

## Par_CostEmission_5_2025
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.052051

## Par_CostEmission_5_2050
Info: Retreived from GENeSYS-MOD data Og regjeringen.no)
Benevning: [EUR/kgCO2e] (0.056)
CostEmisson
0.12479

## Par_Power2Energy_ratio
Info: Generalization of the relation between energy capacity and power capacity when investing in battery capacity. Source: DEA and https://github.com/GENeSYS-MOD/GENeSYS_MOD.data/blob/development/base_year_2021/Data/Parameters/Par_StorageE2PRatio/Par_StorageE2PRatio.csv
Unit: [MW/MWh]
FlexibleLoads | Power2Energy
BESS_Li_Ion_1 | 1
BESS_Redox_1 | 0.25
CAES_1 | 0.1
Flywheel_1 | 1
Hot_Water_Tank_LT_1 | 0.016571
H2_Storage_1 | 0.005988
CH4_Storage_1 | 1

## Par_ChargeEfficiency
Info: Data hentet fra DEA - Teknologirapport - https://ens.dk/sites/ens.dk/files/Analyser/version_7_-_technology_data_catalogue_for_energy_storage.pdf
Unit: Fraction (Brukt 1/0,88) for hydrogen - må "charge" batteriet mer og kompensere for tapet på vei inn i batteriet - derfor efficiency definert slik.
FlexibleLoad | Charge_efficiency
BESS_Li_Ion_1 | 1.0204
BESS_Redox_1 | 1
CAES_1 | 1.1905
Flywheel_1 | 1.0101
Hot_Water_Tank_LT_1 | 1
H2_Storage_1 | 1.1364
CH4_Storage_1 | 1

## Par_DischargeEfficiency
Info: Data hentet fra DEA - Teknologirapport - https://ens.dk/sites/ens.dk/files/Analyser/version_7_-_technology_data_catalogue_for_energy_storage.pdf
Unit: Fraction
FlexibleLoad | Discharge_efficiency
BESS_Li_Ion_1 | 0.97
BESS_Redox_1 | 0.78
CAES_1 | 0.84
Flywheel_1 | 0.99
Hot_Water_Tank_LT_1 | 1
H2_Storage_1 | 1
CH4_Storage_1 | 1

## Par_ECToTech_Efficiency
Info: Tenker vi kan anta null tap på linjene (EC-Tech) siden vi omhandler efficiency for hver teknologi i filen (Tech - EC)
Unit: [-]
Technology | EnergyCarrier | Operational mode | ECToTech_Efficiency
ElectricBoiler | Electricity | 1 | 1
HP_LT | Electricity | 1 | 1
HP_MT | Electricity | 1 | 1
HP_MT | Electricity | 2 | 1
P2G | Electricity | 1 | 1
G2P | H2 | 1 | 1
GasBoiler | CH4_H2_Mix | 1 | 1
GasBoiler | CH4_H2_Mix | 2 | 1
GasBoiler | CH4 | 3 | 1
GasBoiler | CH4 | 4 | 1
GasBoiler | Biogas | 5 | 1
GasBoiler | Biogas | 6 | 1
GasBoiler_CCS | CH4_H2_Mix | 1 | 1
GasBoiler_CCS | CH4_H2_Mix | 2 | 1
GasBoiler_CCS | CH4 | 3 | 1
GasBoiler_CCS | CH4 | 4 | 1
GasBoiler_CCS | Biogas | 5 | 1
GasBoiler_CCS | Biogas | 6 | 1
CHP | CH4_H2_Mix | 1 | 1
CHP | CH4_H2_Mix | 2 | 1
CHP | CH4 | 3 | 1
CHP | CH4 | 4 | 1
CHP | Biogas | 5 | 1
CHP | Biogas | 6 | 1
CHP_CCS | CH4_H2_Mix | 1 | 1
CHP_CCS | CH4_H2_Mix | 2 | 1
CHP_CCS | CH4 | 3 | 1
CHP_CCS | CH4 | 4 | 1
CHP_CCS | Biogas | 5 | 1
CHP_CCS | Biogas | 6 | 1
CH4_H2_Mixer | H2 | 1 | 0.2
CH4_H2_Mixer | CH4 | 1 | 0.8
Power_Grid | Electricity | 2 | 1
Biogas_Grid | Biogas | 2 | 1
CH4_Grid | CH4 | 2 | 1
H2_Grid | H2 | 2 | 1

## Par_TechToEC_Efficiency
Info: Source: DEA
Unit: [-]
Technology | EnergyCarrier | Operational mode | TechToEC_Efficiency
Power_Grid | Electricity | 1 | 1
ElectricBoiler | LT | 1 | 0.99
ElectricBoiler | MT | 2 | 0.99
HP_LT | LT | 1 | 3
HP_MT | MT | 1 | 2
HP_MT | LT | 2 | 3
PV | Electricity | 1 | 1
P2G | H2 | 1 | 0.6
G2P | Electricity | 1 | 0.6
GasBoiler | LT | 1 | 0.93
GasBoiler | MT | 2 | 0.93
GasBoiler | LT | 3 | 0.93
GasBoiler | MT | 4 | 0.93
GasBoiler | LT | 5 | 0.93
GasBoiler | MT | 6 | 0.93
GasBoiler_CCS | LT | 1 | 0.837
GasBoiler_CCS | MT | 2 | 0.837
GasBoiler_CCS | LT | 3 | 0.837
GasBoiler_CCS | MT | 4 | 0.837
GasBoiler_CCS | LT | 5 | 0.837
GasBoiler_CCS | MT | 6 | 0.837
CHP | LT | 1 | 0.45
CHP | Electricity | 1 | 0.3
CHP | MT | 2 | 0.45
CHP | Electricity | 2 | 0.3
CHP | LT | 3 | 0.45
CHP | Electricity | 3 | 0.3
CHP | MT | 4 | 0.45
CHP | Electricity | 4 | 0.3
CHP | LT | 5 | 0.45
CHP | Electricity | 5 | 0.3
CHP | MT | 6 | 0.45
CHP | Electricity | 6 | 0.3
CHP_CCS | LT | 1 | 0.405
CHP_CCS | Electricity | 1 | 0.27
CHP_CCS | MT | 2 | 0.405
CHP_CCS | Electricity | 2 | 0.27
CHP_CCS | LT | 3 | 0.405
CHP_CCS | Electricity | 3 | 0.27
CHP_CCS | MT | 4 | 0.405
CHP_CCS | Electricity | 4 | 0.27
CHP_CCS | LT | 5 | 0.405
CHP_CCS | Electricity | 5 | 0.27
CHP_CCS | MT | 6 | 0.405
CHP_CCS | Electricity | 6 | 0.27
Biogas_Grid | Biogas | 1 | 0.9999
CH4_Grid | CH4 | 1 | 0.9999
CH4_H2_Mixer | CH4_H2_Mix | 1 | 1
DieselReserveGenerator | Electricity | 1 | 0.37
H2_Grid | H2 | 1 | 0.9999

## Par_InitialCapacityInstalled
Info: Electric Boilers and Heat Pump size: https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_industrial_process_heat.pdf. PV: https://coldwellsolar.com/commercial-solar-blog/what-kind-of-solar-array-is-needed-to-power-an-industrial-plant/ , P2G: https://en.wikipedia.org/wiki/Power-to-gas G2P: https://petrowiki.spe.org/Gas_to_power . For GasBoiler: https://www.linkedin.com/pulse/gas-fired-boilers-market-analysis-report-global-insights-region-7ccbc For CHP: https://iea.blob.core.windows.net/assets/d459f7d5-1ba7-49d9-ad56-915fba22f267/chp_report.pdf
Unit: [MW] (PV initially 5)
Technology | Initial_Installed_Capacity
Power_Grid | 2000
ElectricBoiler | 1121.964
HP_LT | 32.186
HP_MT | 0
PV | 0
P2G | 0
G2P | 0
GasBoiler | 0
GasBoiler_CCS | 0
CHP | 0
CHP_CCS | 0
Biogas_Grid | 1000
CH4_Grid | 1000
CH4_H2_Mixer | 0
DieselReserveGenerator | 0
H2_Grid | 1000

## Par_InitialSoC
Info: Assume flexible Loads at full load
Unit: Fraction
FlexibleLoad | InitialSoC
BESS_Li_Ion_1 | 0.5
BESS_Redox_1 | 0.5
CAES_1 | 0.5
Flywheel_1 | 0.5
Hot_Water_Tank_LT_1 | 0.5
H2_Storage_1 | 0.5
CH4_Storage_1 | 0.5

## Par_MaxChargeDischargeRate
Info: https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf
Unit: [MW] til flexible load (sammenlignet med effekstærrelse i MaxCapacity
FlexibleLoad | Max_charge_discharge_rate
BESS_Li_Ion_1 | 0
BESS_Redox_1 | 0
CAES_1 | 0
Flywheel_1 | 10
Hot_Water_Tank_LT_1 | 0
H2_Storage_1 | 0
CH4_Storage_1 | 0

## Par_MaxStorageCapacity
Info: all parameters: https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf
Unit: [MWh]
FlexibleLoad | MaxStorageCapacity
BESS_Li_Ion_1 | 0
BESS_Redox_1 | 0
CAES_1 | 0
Flywheel_1 | 10
Hot_Water_Tank_LT_1 | 0
H2_Storage_1 | 0
CH4_Storage_1 | 0

## Par_MaxDwnShift
Info:
Unit: fraction of demand that can be shifted
Time | MaximumDwnShift
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 0
8 | 0.3
9 | 0.3
10 | 0.3
11 | 0.3
12 | 0.3
13 | 0.3
14 | 0.3
15 | 0.3
16 | 0.3
17 | 0.3
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0

## Par_MaxUpShift
Time | MaximumUpShift
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 0
8 | 0.1
9 | 0.1
10 | 0.1
11 | 0.1
12 | 0.1
13 | 0.1
14 | 0.1
15 | 0.1
16 | 0.1
17 | 0.1
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0

## Par_MaxExport
Info: Kan ikke eksportere mer enn totalt demand
Unit: [MWh/year]
MaxExport
130000

## Par_SelfDischarge
Info: Data hentet fra DEA - Teknologirapport - https://ens.dk/sites/ens.dk/files/Analyser/version_7_-_technology_data_catalogue_for_energy_storage.pdf
Unit: Fraction loss per hour, t
FlexibleLoad | SelfDischarge
BESS_Li_Ion_1 | 4.1667e-05
BESS_Redox_1 | 0
CAES_1 | 0
Flywheel_1 | 0.00125
Hot_Water_Tank_LT_1 | 8.3333e-05
H2_Storage_1 | 0.00041667
CH4_Storage_1 | 0

## Set_of_EnergyCarrier
EnergyCarrier
Electricity
LT
MT
H2
CH4
Biogas
CH4_H2_Mix

## Set_of_FlexibleLoad
FlexibleLoad
BESS_Li_Ion_1
BESS_Redox_1
CAES_1
Flywheel_1
Hot_Water_Tank_LT_1
H2_Storage_1
CH4_Storage_1

## Set_of_FlexibleLoadForEC
FlexibleLoad | EnergyCarrier
BESS_Li_Ion_1 | Electricity
BESS_Redox_1 | Electricity
CAES_1 | Electricity
Flywheel_1 | Electricity
Hot_Water_Tank_LT_1 | LT
H2_Storage_1 | H2
CH4_Storage_1 | CH4

## Set_of_Month
Month
1

## Par_Ramping_factor
Technology | Ramping factor
Power_Grid | 1
ElectricBoiler | 1
HP_LT | 1
HP_MT | 1
PV | 1
P2G | 1
G2P | 1
GasBoiler | 1
GasBoiler_CCS | 1
CHP | 1
CHP_CCS | 1
Biogas_Grid | 1
CH4_Grid | 1
CH4_H2_Mixer | 1
DieselReserveGenerator | 1
H2_Grid | 1

## Set_of_Technology
Technology
Power_Grid
ElectricBoiler
HP_LT
HP_MT
PV
P2G
G2P
GasBoiler
GasBoiler_CCS
CHP
CHP_CCS
Biogas_Grid
CH4_Grid
CH4_H2_Mixer
DieselReserveGenerator
H2_Grid

## Subset_ECToTech
Technology | EnergyCarrier | Operational mode
ElectricBoiler | Electricity | 1
HP_LT | Electricity | 1
HP_MT | Electricity | 1
HP_MT | Electricity | 2
P2G | Electricity | 1
G2P | H2 | 1
GasBoiler | CH4_H2_Mix | 1
GasBoiler | CH4_H2_Mix | 2
GasBoiler | CH4 | 3
GasBoiler | CH4 | 4
GasBoiler | Biogas | 5
GasBoiler | Biogas | 6
GasBoiler_CCS | CH4_H2_Mix | 1
GasBoiler_CCS | CH4_H2_Mix | 2
GasBoiler_CCS | CH4 | 3
GasBoiler_CCS | CH4 | 4
GasBoiler_CCS | Biogas | 5
GasBoiler_CCS | Biogas | 6
CHP | CH4_H2_Mix | 1
CHP | CH4_H2_Mix | 2
CHP | CH4 | 3
CHP | CH4 | 4
CHP | Biogas | 5
CHP | Biogas | 6
CHP_CCS | CH4_H2_Mix | 1
CHP_CCS | CH4_H2_Mix | 2
CHP_CCS | CH4 | 3
CHP_CCS | CH4 | 4
CHP_CCS | Biogas | 5
CHP_CCS | Biogas | 6
CH4_H2_Mixer | H2 | 1
CH4_H2_Mixer | CH4 | 1
Power_Grid | Electricity | 2
Biogas_Grid | Biogas | 2
CH4_Grid | CH4 | 2
H2_Grid | H2 | 2

## Subset_TechToEC
Technology | EnergyCarrier | Operational mode
Power_Grid | Electricity | 1
ElectricBoiler | LT | 1
ElectricBoiler | MT | 2
HP_LT | LT | 1
HP_MT | MT | 1
HP_MT | LT | 2
PV | Electricity | 1
P2G | H2 | 1
G2P | Electricity | 1
GasBoiler | LT | 1
GasBoiler | MT | 2
GasBoiler | LT | 3
GasBoiler | MT | 4
GasBoiler | LT | 5
GasBoiler | MT | 6
GasBoiler_CCS | LT | 1
GasBoiler_CCS | MT | 2
GasBoiler_CCS | LT | 3
GasBoiler_CCS | MT | 4
GasBoiler_CCS | LT | 5
GasBoiler_CCS | MT | 6
CHP | LT | 1
CHP | Electricity | 1
CHP | MT | 2
CHP | Electricity | 2
CHP | LT | 3
CHP | Electricity | 3
CHP | MT | 4
CHP | Electricity | 4
CHP | LT | 5
CHP | Electricity | 5
CHP | MT | 6
CHP | Electricity | 6
CHP_CCS | LT | 1
CHP_CCS | Electricity | 1
CHP_CCS | MT | 2
CHP_CCS | Electricity | 2
CHP_CCS | LT | 3
CHP_CCS | Electricity | 3
CHP_CCS | MT | 4
CHP_CCS | Electricity | 4
CHP_CCS | LT | 5
CHP_CCS | Electricity | 5
CHP_CCS | MT | 6
CHP_CCS | Electricity | 6
Biogas_Grid | Biogas | 1
CH4_Grid | CH4 | 1
CH4_H2_Mixer | CH4_H2_Mix | 1
DieselReserveGenerator | Electricity | 1
H2_Grid | H2 | 1

## Set_Mode_of_Operation
Operational mode
1
2
3
4
5
6

## Par_BatteryCost
Unit: [EUR/MWh]
FlexibleLoad | Cost
BESS_Li_Ion_1 | 2.02
BESS_Redox_1 | 0.957
CAES_1 | 2.616
Flywheel_1 | 0
Hot_Water_Tank_LT_1 | 0
H2_Storage_1 | 0
CH4_Storage_1 | 0

## Par_Cost_LS
EnergyCarrier | CostLS
Electricity | 1
LT | 1
MT | 1
H2 | 0
CH4 | 1
Biogas | 0
CH4_H2_Mix | 0

## Par_Max_Capex_tec
Technology | Capex
Power_Grid | 100000
ElectricBoiler | 100000
HP_LT | 100000
HP_MT | 100000
PV | 100000
P2G | 100000
G2P | 100000
GasBoiler | 100000
GasBoiler_CCS | 100000
CHP | 100000
CHP_CCS | 100000
Biogas_Grid | 100000
CH4_Grid | 100000
CH4_H2_Mixer | 100000
DieselReserveGenerator | 100000
H2_Grid | 100000

## Par_Max_Capex_bat
FlexibleLoad | Capex
BESS_Li_Ion_1 | 100000
BESS_Redox_1 | 100000
CAES_1 | 100000
Flywheel_1 | 100000
Hot_Water_Tank_LT_1 | 100000
H2_Storage_1 | 100000
CH4_Storage_1 | 100000

## Par_Max_CAPEX
Max CAPEX
100000000

## Par_Max_Carbon_Emission
Max Carbon E
1000000